Nisource Distribution Companies

Gas Quality Tariff Provisions

General Statement


The gas quality tariff provisions for the various NI LDC’ s are few. Some are as general as referring to pipeline quality gas. In any event, below is a capsulation of seven LDC’s tariff provisions. 

LDC #1   

a) Heat Value greater than or equal to 950 btu via recording calorimeters; less than or equal to a trace of  Hydrogen Sulfide, per 100 cubic feet of gas; less than or equal to 20 grains  Total Sulfur per 100 cubic feet of gas. Otherwise,

b) Commercially free from dust or liquid matter which might interfere with its merchantability or cause injury to or interference with proper operation of the lines, regulators, meters, and other equipment of customer.

c) Wobbe index 1300, plus or minus 6%.

LDC #2

a) Gas delivered through an interstate pipeline to the Company, by or on behalf of the customer, shall conform to the interstate pipeline’s FERC approved gas quality standards. Gas not delivered through an interstate pipeline must be of a certain quality as determined by the Company. 

LDC #3

a) Gas delivered by or on behalf of Customer to Company at point(s) of receipt with an interstate pipeline shall conform to the interstate pipeline’s gas quality standards.

b) At points of receipt other than an interstate pipeline, gas shall be commercially free from oil, water, salt, dust, gum, gum forming constituents, harmful or noxious vapors, or other solid or liquid matter which might interfere with its merchantability or cause to or interference with proper operation of the lines, regulators, meters, and other equipment of Company or its customers.

c) Gas delivered shall not contain in excess of 

-Five pounds of water per million cubic feet

-Three percent (3%) by volume of a combined total of carbon dioxide and nitrogen components.

· Twenty-five hundredths (0.25) grains of hydrogen sulfide per one hundred (100) cubic feet of gas; and

· Ten (10) grains of sulfur per one hundred(100) cubic feet of gas.

· Heating value of not less than 1000 btu per standard cubic foot and have a Utilization Factor (Wobbe) of 1300 , plus or minus 6 %.

LDC #4 ,5 and 6


Pipeline quality natural gas( refer to pipelines’ tariff)

LDC #7


It is shipper’s obligation to provide gas of suitable quality to the company at the agreed upon delivery points.

